## lux table
Illumination and Design Table
1sq.ft=0.0929 sq.m
73.54
ILLUMINATION TABLE DESIGN
[11 empty] | 1SQ.FT= | 0.0929 sq.m
S.N | Location/Floor | Details | Standard Lux | Required Lux€ | Area (sq. ft) | Area (sq. meter)-(A) | Utilization factor | Maintainance Facor | Effeciency (lumen/Watt) | Wattage per bulb | Lamp Flux in Lumen (Φ) | Light Fixture(s) Used | No of Lamp per luminairies | No of Lumenaries | Corrected no of Lumenaries(N) | Total Watts
1 | Basement Floor Plan | 18 Car Parking | 20-30-50 | 50 | 2923.2029 | 271.5655 | 0.8 | 0.8 | 125 | 36 | 4500 | Titania Plus T8 LED TUBE | 1 | 4.7147 | 6 | 216
|  | Other Cars | 20-30-50 | 50 | 2629.6536 | 244.2948 | 0.8 | 0.8 | 125 | 36 | 4500 | Titania Plus T8 LED TUBE | 1 | 4.2412 | 5 | 180
|  | Stairs | 50-100-150 | 150 | 219.886 | 20.4274 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.9151 | 2 | 50
|  | Guard Room | 50-100-150 | 150 | 61.0777 | 5.6741 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.209 | 2 | 26
|  | Store | 50-100-150 | 150 | 96.9213 | 9.004 | 0.8 | 0.8 | 85 | 10 | 600 | Phillips Green Ledi | 1 | 3.5172 | 4 | 40
|  | Electrical Duct | 50-100-150 | 50 | 23.5283 | 2.1858 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.94869 | 1 | 11
|  | Transformer Unit | 100-150-200 | 200 | 128.9783 | 11.9821 | 0.8 | 0.8 | 133 | 45 | 3985 | Canopy Light | 1 | 0.93962 | 1 | 45
|  | Bike Parking | 20-30-50 | 50 | 2421.3208 | 224.9407 | 0.8 | 0.8 | 125 | 36 | 4500 | Titania Plus T8 LED TUBE | 1 | 3.9052 | 4 | 144
|  | Aune Slop | 20-30-50 | 50 | 442.9767 | 41.1525 | 0.8 | 0.8 | 130 | 23 | 3000 | Consta Pro LED Strip Light | 1 | 1.0717 | 1 | 23
2 | Ground Floor Plan | [14 empty] | 0
|  | Office 1 | 300-500-750 | 400 | 1504.6206 | 139.7793 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 19.855 | 19 | 494
|  | Washroom office1 | 50-100-150 | 150 | 59.3326 | 5.512 | 0.8 | 0.8 | 85 | 10 | 1400 | Philips Greenledi | 1 | 0.92277 | 1 | 10
|  | Generator Room | 100-150-200 | 200 | 82.2869 | 7.6445 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 2.1717 | 3 | 39
|  | Fire staircase going room | 150-200-300 | 150 | 417.8441 | 38.8177 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 2.0677 | 3 | 78
|  | Lobby | 150-200-300 | 150 | 245.581 | 22.8145 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.2153 | 2 | 52
|  | Staircase | 50-100-150 | 150 | 216.096 | 20.0753 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.8821 | 2 | 50
|  | Electrical Duct | 50-100-150 | 50 | 23.4113 | 2.1749 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.94397 | 1 | 11
|  | Coffee Shop | 150-200-300 | 200 | 1503.9722 | 139.719 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 9.9232 | 10 | 260
|  | Fitting room 1(mango store) | 50-100-150 | 95 | 12.8334 | 1.1922 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.98317 | 1 | 11
|  | Fitting room2(Mango store) | 50-100-150 | 95 | 12.8334 | 1.1922 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.98317 | 1 | 11
|  | Store | 50-100-150 | 150 | 380.4574 | 35.3445 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.8827 | 2 | 52
|  | Mango Store | 150-200-300 | 300 | 1668.8144 | 155.0329 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 16.5163 | 17 | 442
|  | Staircase(Mango Store) | 50-100-150 | 150 | 124.5 | 11.566 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.0843 | 2 | 50
|  | W2f5c1 | 150-200-300 | 150 | 24.0737 | 2.2364 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.87361 | 1 | 10
|  | Fire Staircase | 50-100-150 | 150 | 79.9087 | 7.4235 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.5817 | 2 | 26
[6 empty] | 590.525 | [9 empty] | 0
3 | First Floor Plan | Office 3 | 300-500-750 | 400 | 1504.8267 | 139.7984 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 19.8577 | 21 | 546
|  | Entrance to washroom | 150-200-300 | 200 | 16.671 | 1.5487 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.80663 | 1 | 10
|  | washroom w1f2CO | 50-100-150 | 200 | 30.9169 | 2.8722 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.4959 | 2 | 20
|  | Another washroom D2V! | 50-100-150 | 100 | 40.0032 | 3.7163 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.96779 | 1 | 10
|  | Fire Staircase | 50-100-150 | 150 | 79.9087 | 7.4235 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.5817 | 2 | 26
|  | Stair | 50-100-150 | 150 | 214.2128 | 19.9004 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.8657 | 2 | 50
|  | Electrical Duct | 50-100-150 | 50 | 23.4113 | 2.1749 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.94397 | 1 | 11
|  | Office 2 | 300-500-750 | 400 | 1866.5884 | 173.4061 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 24.6315 | 26 | 676
|  | Drawing Room | 50-100-150 | 150 | 14.9166 | 1.3858 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 1.8044 | 2 | 22
|  | Stair to go to office 2 | 50-100-150 | 150 | 130.8384 | 12.1549 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.1395 | 2 | 50
|  | Washroom in trapezium room | 50-100-150 | 150 | 49.0769 | 4.5592 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.781 | 2 | 20
|  | Box inside trapezium area | 50-100-150 | 150 | 14.0822 | 1.3082 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.51103 | 1 | 10
|  | Looby type to go washroom | 50-100-150 | 150 | 100.3164 | 9.3194 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.9857 | 2 | 26
|  | Riser Tread | 50-100-150 | 150 | 201.55 | 18.724 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight |  | 3.9895 | 4 | 52
|  | Lobby | 150-200-300 | 150 | 244.2639 | 22.6921 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.2087 | 2 | 52
|  | Fire Staircase Entrance | 150-200-300 | 150 | 297.3679 | 27.6255 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 5.8861 | 6 | 78
|  | Drawing Room 2 | 50-100-150 | 150 | 14.9166 | 1.3858 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 1.8044 | 2 | 22
449.9953
4 | Second Floor Plan
|  | Office 4 | 300-500-750 | 400 | 1328.9864 | 123.4628 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 17.5373 | 17 | 442
|  | Lobby to washroomm | 50-100-150 | 150 | 17.5962 | 1.6347 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.63855 | 1 | 10
|  | Washroom D2 office 4 | 50-100-150 | 150 | 28.2256 | 2.6222 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.0243 | 1 | 10
|  | Basin room | 50-100-150 | 150 | 26.0764 | 2.4225 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.94629 | 1 | 10
|  | Office 5 | 300-500-750 | 400 | 2106.6665 | 195.7093 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 27.7996 | 31 | 806
|  | Lobby to washroom office 5 | 50-100-150 | 150 | 16.6709 | 1.5487 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.60497 | 1 | 10
|  | Washroom D2 office 5 | 50-100-150 | 100 | 30.6699 | 2.8492 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.74199 | 1 | 10
|  | Basin room office 5 | 50-100-150 | 100 | 31.5419 | 2.9302 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.76308 | 1 | 10
|  | Fire Staircase Entrance | 150-200-300 | 150 | 302.3332 | 28.0868 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 5.9844 | 6 | 78
|  | Fire Staircase | 50-100-150 | 150 | 79.9087 | 7.4235 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.5817 | 2 | 26
|  | Lobby | 150-200-300 | 150 | 241.3108 | 22.4178 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.1941 | 2 | 52
|  | Stair | 50-100-150 | 150 | 195.0569 | 18.1208 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.6988 | 2 | 50
|  | Electrical Duct | 50-100-150 | 50 | 23.8779 | 2.2183 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.96279 | 1 | 11
411.4468
5 | Third Floor To Fifth Floor Plan
|  | Office 6 | 300-500-750 | 400 | 1247.5188 | 115.8945 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 16.4623 | 18 | 468
|  | Wahsfroom lobby office 6 | 50-100-150 | 150 | 17.5962 | 1.6347 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.63855 | 1 | 10
|  | washroom | 50-100-150 | 150 | 29.84 | 2.7721 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.0829 | 1 | 10
|  | Basin Room | 50-100-150 | 150 | 28.3315 | 2.632 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.0281 | 1 | 10
|  | Office 7 | 300-500-750 | 400 | 2013.7808 | 187.0802 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 26.5739 | 28 | 728
|  | Washroom lobby office 7 | 50-100-150 | 150 | 16.1058 | 1.4962 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.58446 | 1 | 10
|  | wahshroom | 50-100-150 | 150 | 24.8689 | 2.3103 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.90247 | 1 | 10
|  | Basin Room | 50-100-150 | 150 | 30.6148 | 2.8441 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.111 | 2 | 20
|  | Office 8 | 300-500-750 | 400 | 1622.9298 | 150.7702 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 21.4162 | 22 | 572
|  | Washroom Lobby office 8 | 50-100-150 | 150 | 16.6708 | 1.5487 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.60497 | 1 | 10
|  | Washroom | 50-100-150 | 150 | 31.5422 | 2.9303 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.1446 | 2 | 20
|  | Basin Room | 50-100-150 | 150 | 28.9533 | 2.6898 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.0507 | 1 | 10
|  | Stair | 50-100-150 | 150 | 201.6523 | 18.7335 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.7563 | 2 | 50
|  | Fire Staircase | 50-100-150 | 150 | 79.9087 | 7.4235 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.5817 | 2 | 26
|  | Electrical Duct | 50-100-150 | 50 | 24.8002 | 2.3039 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.99997 | 1 | 11
|  | Lobby | 150-200-300 | 150 | 245.3815 | 22.7959 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.2143 | 2 | 52
|  | Fire Staircase Entrance | 150-200-300 | 150 | 301.43 | 28.0028 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 5.9665 | 6 | 78
553.8629
6 | Top Floor Plan
|  | Office 15 | 300-500-750 | 400 | 2170.6791 | 201.6561 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 28.6443 | 30 | 780
|  | Washroom Lobby | 50-100-150 | 150 | 16.6129 | 1.5433 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.60287 | 1 | 10
|  | Washroom | 50-100-150 | 150 | 28.2256 | 2.6222 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 1.0243 | 1 | 10
|  | Basin | 50-100-150 | 150 | 26.0764 | 2.4225 | 0.8 | 0.8 | 85 | 10 | 600 | Philips Greenledi | 1 | 0.94629 | 1 | 10
|  | Fire Staircase Entrance | 150-200-300 | 150 | 307.8365 | 28.598 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 6.0933 | 6 | 78
|  | Staircase | 50-100-150 | 150 | 211.3458 | 19.634 | 0.8 | 0.8 | 100 | 25 | 2500 | Coreline Downlight | 1 | 1.8407 | 2 | 50
|  | Lobby | 150-200-300 | 150 | 265.2891 | 24.6454 | 0.8 | 0.8 | 120 | 26 | 4400 | Hercules LED PANEL | 1 | 1.3128 | 2 | 52
|  | Electrical Duct | 50-100-150 | 50 | 23.2949 | 2.1641 | 0.8 | 0.8 | 60 | 11 | 180 | ADORE LED LAMP DIM A19-11W 5K E26 | 1 | 0.93928 | 1 | 11
|  | Fire Staircase | 50-100-150 | 150 | 79.9087 | 7.4235 | 0.8 | 0.8 | 85 | 13 | 1100 | Coreline Slim Downlight | 1 | 1.5817 | 2 | 26
290.7091

## Tp mccb calculation
FLOOR | DB_Boxes | Power circuit | POWER WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL POWER CIRCUIT WATT | TOTAL LIGHT CIRCUIT WATT | TOTAL WATTS | CURRENT RATING | RATING OF MCB /MCCB USED(AFTER SDB) | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
Basement floor Plan | SDB1 | 11 | 500 | 0 | 0 | 5500 | 0 | 5500 | 22.4185 | 32A, DP MCB | 18.5592 | 40A, TP MCCB
| SDB 2 | 4 | 500 | 2 | 13 | 2000 | 609 | 2609 | 10.6345 | 20A, DP MCB
|  |  |  | 2 | 10
|  |  |  | 15 | 36
|  |  |  | 1 | 23
| SDB 3 | 10 | 500 | 1 | 11 | 5000 | 106 | 5106 | 20.8125 | 32A, DP MCB
|  |  |  | 1 | 45
|  |  |  | 2 | 25
| BFDB | 1 | 500 | 0 | 0 | 500 | 0 | 500 | 2.038 | -
TOTAL: | [7 empty] | 13715
[10 empty] | MDB MCCB RATING= | 299.3965 | 300A
245742
307177.5
FLOOR | DB_Boxes | Power circuit | POWER WATT | AC SOCKET | AC WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL LIGHT CIRCUIT WATT | TOTAL POWER CIRCUIT WATT | TOTAL WATTS | Total Current | Rating of MCB/MCCB USED | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
Ground Floor Plan | SDB 1 | 23 | 500 | 3 | 1250 | 19 | 26 | 647 | 15250 | 15897 | 21.5119 | 32A, TP MCCB | 50.1159 | 63A, TPMCCB
[6 empty] | 1 | 10
[6 empty] | 3 | 13
[6 empty] | 2 | 13
[6 empty] | 3 | 26
| SDB 2 | 20 | 500 | 1 | 1250 | 10 | 26 | 260 | 11250 | 11510 | 15.5754 | 20A, TP MCCB
| SDB 3 | 13 | 500 | 0 | 1250 | 21 | 26 | 628 | 6500 | 7128 | 9.6456 | 20A, TP MCCB
[6 empty] | 2 | 25
[6 empty] | 2 | 11
[6 empty] | 1 | 10
| GFDB | 5 | 500 | 0 | 1250 | 0 | 0 | 0 | 2500 | 2500 | 10.1902 | -
TOTAL: | [9 empty] | 37035
FLOOR | DB_Boxes | Power circuit | POWER WATT | AC SOCKET | AC WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL LIGHT CIRCUIT WATT | TOTAL POWER CIRCUIT WATT | TOTAL WATTS | Total Current | Rating of MCB/MCCB USED | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
FIRST FLOOR PLAN | SDB1 | 40 | 500 | 1 | 1250 | 21 | 26 | 730 | 21250 | 21980 | 29.7434 | 32A, TP MCCB | 53.3135 | 63A, TPMCCB
[6 empty] | 3 | 10
[6 empty] | 8 | 13
[6 empty] | 2 | 25
|  | 15 | 500 | 4 | 1250 | 28 | 26 | 800 | 12500 | 13300 | 17.9976 | 20A, TP MCCB
[6 empty] | 2 | 11
[6 empty] | 2 | 25
| SDB 3 | 7 | 500 | 0 | 1250 | 3 | 10 | 108 | 3500 | 3608 | 14.7065 | 20A, DP MCB
[6 empty] | 6 | 13
| FFDB | 1 | 500 | 0 | 1250 | 1 | 10 | 10 | 500 | 510 | 2.0788 | -
TOTAL: | [9 empty] | 39398
FLOOR | DB_Boxes | Power circuit | POWER WATT | AC SOCKET | AC WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL LIGHT CIRCUIT WATT | TOTAL POWER CIRCUIT WATT | TOTAL WATTS | Total Current | Rating of MCB/MCCB USED | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
SECOND FLOOR PLAN | SDB1 | 41 | 500 | 0 | 1250 | 26 | 31 | 990 | 20500 | 21490 | 29.0804 | 32A, TP MCCB | 49.7641 | 63A, TPMCCB
[6 empty] | 3 | 10
[6 empty] | 6 | 13
[6 empty] | 2 | 13
[6 empty] | 2 | 25
| SDB 2 | 21 | 500 | 3 | 1250 | 19 | 26 | 524 | 14250 | 14774 | 19.9922 | 25A, TP MCCB
[6 empty] | 3 | 10
| SFDB | 1 | 500 | 0 | 1250 | 1 | 11 | 11 | 500 | 511 | 2.0829 | -
TOTAL: | [9 empty] | 36775
FLOOR | DB_Boxes | Power circuit | POWER WATT | AC SOCKET | AC WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL LIGHT CIRCUIT WATT | TOTAL POWER CIRCUIT WATT | TOTAL WATTS | Total Current | Rating of MCB/MCCB USED | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
Third to fifth floor plan | SDB1 | 35 | 500 | 3 | 1250 | 23 | 26 | 772 | 21250 | 22022 | 29.8003 | 32A, TP MCCB | 85.7269 | 100A, TP MCCB
[6 empty] | 2 | 10
[6 empty] | 8 | 13
[6 empty] | 2 | 25
| SDB 2 | 38 | 500 | 2 | 1250 | 28 | 26 | 768 | 21500 | 22268 | 30.1332 | 32A, TP MCCB
[6 empty] | 4 | 10
| TFDB | 32 | 500 | 2 | 1250 | 20 | 26 | 561 | 18500 | 19061 | 25.7934 | -
[6 empty] | 3 | 10
[6 empty] | 1 | 11
TOTAL: | [9 empty] | 63351
FLOOR | DB_Boxes | Power circuit | POWER WATT | AC SOCKET | AC WATT | NO OF LIGHT | WATTAGE OF LIGHT | TOTAL LIGHT CIRCUIT WATT | TOTAL POWER CIRCUIT WATT | TOTAL WATTS | Total Current | Rating of MCB/MCCB USED | 3 PHASELINE CURRENT OF FDB | MCCB RATING USED
Top Floor plan | SDB1 | 49 | 500 | 4 | 1250 | 32 | 26 | 966 | 29500 | 30466 | 41.2267 | 50A, TP MCCB | 41.9169 | 50A, TP MCCB
[6 empty] | 8 | 13
[6 empty] | 3 | 10
| TOPFDB | 1 | 500 | 0 | 1250 | 1 | 10 | 10 | 500 | 510 | 2.0788 | -
TOTAL: | [9 empty] | 30976